## Slide 1
2019 European Seminar – Amsterdam, Netherlands

## Slide 2
IoT Cloud Firmware (V4.9)

## Slide 3
Vivotek CCTV Integration

## Slide 5
License Plate Recognition
{
“plate”: {
“number”: “SN64WZO”}
}

## Slide 6
BACnet Secure Connect

## Slide 7
BACnet Secure Connect
What is BACnet/SC?
Addendum to BACnet
Adds encryption and authentication to native BACnet

## Slide 13
Network Port Security
(IEEE 802.1X)

## Slide 14
IEEE 802.1X
Why?
Provides a higher level of security – may be mandated by IT
What is it?
is an IEEE Standard for port-based Network Access Control
it provides an authentication mechanism to devices wishing to attach to a LAN or WLAN

## Slide 15
How IEEE 802.1X works
3 Parties
  Supplicant – client wishing to attach to network
  Authenticator – network device providing data link
  Authentication Server – trusted server that responds to network access requests
  Supplicant
  Authenticator
  Authentication Server
Notes: Supplicant – client wishing to attach
Authenticator – network device providing a datalink between client and network (and can block traffic) – switch or wireless access point
Authentication server – trusted server that can receive and respond to requests for network access

## Slide 16
How IEEE 802.1X Authenticates
Uses EAP (Extensible Authentication Protocol)
Many authentication methods.
  EAP-TLS is widely supported. Uses digital certificates to authenticate the supplicant and authentication server
CA Root Certificate
Client Certificate
Server Certificate
Notes: Good to understand how EAP-TLS works to understand the workflow

## Slide 17
IEEE 802.1X NP Changes
Part of NP4 – Ethernet 1
Requires
  Identity
  Private Key and Password (if set)
  Client Certificate
  Certificate Authority (CA) Root certificate
Notes: Discuss workflow

## Slide 18
IoT Cloud Ingestion

## Slide 19
Notes: Start with Why, discuss the How and end with the What

## Slide 26
Disrupted Markets

## Slide 27
Notes: Start with Why, discuss the How and end with the What

## Slide 28
Notes: Representation of the physical world in a digital environment
Digital Twin / Device Twin / Device Shadow / IoT Shadow / etc

## Slide 29
Notes: This allows detailed analysis of operational performance without interference. Analytics and simulations can be run to provide guidance for future enhancements

## Slide 30
Notes: From cities…
…to vessels…
…to individual machines…

## Slide 31
Notes: …plant and equipment…

## Slide 32
Evolution of the IoT
Notes: How the IoT is the next stage in a logical sequence

## Slide 33
Notes: Start with Why, discuss the How and end with the What

## Slide 34
Notes: Two candidates:
MQTT – has established itself already
CoAP – possibly a better solution, but has lost ground

## Slide 36: Digital Twin / IoT Shadow
{ "desired":{ "gate-ref":"Gate-A01", "operator":"LH", "flight-number":"3429", "aircraft-type":"CR9", "call-sign":"DLH3AK", "terminal":"T1", "stand":"7", "arrival-departure":"A", "ELDT":"", "scheduled":"12/03/2019 08:11", "probable":"12/02/2019 08:30", "actual":"12/03/2019 08:23", "estimated":"12/02/2019 07:55", "finals":"", "gate-status":"Standby - unoccupied", "light-level":"198lx", "space-temp":"20.5°C", "prescence-detected":"false", "sun-shades":"50%", "AHU-Frost-Stat-Setpoint":"2.0C", "AHU-Heating-Demand-OAT-Hold-Off-Setpoint":"5.0", "AHU-Off-Frost-Coil-Temp":"16.4C", "AHU-Supply-Air-Temp":"17.4C", "AHU-Frost-Coil-Demand":"0%", "AHU-Heating-Coil-Demand":"25%", "AHU-Supply-Fan-Speed-Setpoint":"70%", "AHU-Supply-Fan-Startup-Time":"2.0 min", "AHU-LTHW-Hold-Off-above-OAT-Setpoint":"5C", "AHU-LTHW-Hold-Off-Temp-Setpoint":"50C", "AHU-Off-Frost-Temp-Setpoint":"5C", "AHU-Supply-Air-Temp-Setpoint":"18C", "AHU-Frost-Stat-Healthy":"Normal", "AHU-Intake-Damper-Open":"Open", "AHU-Supply-Fan-DPS":"Flow", "AHU-Intake-Damper-Enable":"Enabled", "AHU-Supply-Fan-Enable":"Enabled", "AHU-Bag-Filter-DPS":"Normal", "AHU-Panel-Filter-DPS":"Normal", "AHU-Frost-Stat-Manual-Lockout":"Normal", "AHU-Intake-Damper-Mismatch":"Normal", "AHU-Supply-Fan-Fault":"Normal", "AHU-LTHW-Heating-Demand":"On", "AHU-Supply-Air-Temp-Sensor-Failed":"Normal", "AHU-Off-Frost-Coil-Temp-Sensor-Failed":"Normal", "AHU-Bag-Filter-Dirty":"Normal", "AHU-Panel-Filter-Dirty":"Normal", "AHU-Off-Frost-Coil-Temp-Sensor-Failed-Alarm":"Normal", "AHU-Panel-Filter-Dirty-Alarm":"Normal", "AHU-Bag-Filter-Dirty-Alarm":"Normal", "AHU-Off-Frost-Coil-Temp-Limit":"Normal", "AHU-Frost-Stat-Tripped-Alarm":"Normal", "AHU-Supply-Fan-Fault-Alarm":"Normal", } }
"finals":"", "gate-status":"Standby - unoccupied", "light-level":"198lx", "space-temp":"20.5°C", "prescence-detected":"false", "sun-shades":"50%", "AHU-Frost-Stat-Setpoint":"2.0C", "AHU-Heating-Demand-OAT-Hold-Off-Setpoint":"5.0", "AHU-Off-Frost-Coil-Temp":"16.4C", "AHU-Supply-Air-Temp":"17.4C",
Notes: Different IoT providers have different themes of the same services – this is AWS

## Slide 37
Notes: The number of connections is growing exponentially…

## Slide 38
Notes: Security has to be of paramount concern…

## Slide 39
Notes: Cybersecurity is the most critical aspect.
TLS provides the lastest and greatest security – Certificates and pre-shared encryption keys, but this is an evolving space
Internet Engineering Task Force provide leadership and other techniques may come to improve TLS – HIP / Cryptoprocessors…

## Slide 40
Google MQTT Bridge